## Substations
Substation Records
Sub Name | Sub Num | Nominal kV(max) | Grounding Resistance (Ohms) | Latitude | Longitude
Springfield | 1 | 345 | 1.1 | 38.7175 | -98.272
Note on A1: Scott R. Dahman: Buses must be assigned to substations (especially transformer buses in the GIC study footprint). PowerWorld can provide bus-substation assignments to Simulator GIC customers for FERC715 cases.
Note on D2: Scott R. Dahman: The resistance in ohms between the substation neutral and earth ground (zero-potential reference). An actual “fall of potential” test is the best way to determine this value. It is very important to specify this value for all substations with grounded transformers. There is not a reliable method for estimating it.
Note on E2: Scott R. Dahman: PowerWorld can provide these values to Simulator GIC customers for FERC715 cases
Note on F2: Scott R. Dahman: PowerWorld can provide these values to Simulator GIC customers for FERC715 cases. Western hemisphere longitudes have a negative sign.

## Transformers Simple
GIC Transformers
Sub Name High | Nom kV High | Nom kV Med | Nom kV Ter | Bus Num High | Bus Name High | Bus Num Med | Bus Name Med | Bus Num Ter | Bus Name Ter | Circuit | Coil Resistance (Ohms) for High winding | Coil Resistance (Ohms) for Medium winding | XF Config High | XF Config Med | Is Autotransformer | Core Type
Springfield | 345 | 18 |  | 1 | Springfield1 | 2 | Springfield2 | 0 |  | 1 | 0.138 | 0.0012 | Gwye | Delta | NO | Single Phase
Note on A1: Scott R. Dahman: Simple format if data is to be provided for PowerWorld or another consultant to input into modeling software
Note on L2: Scott R. Dahman: DC resistance in ohms, per phase. (Values for ungrounded delta windings are generally not needed as these are open circuits to GIC.)
Note on M2: Scott R. Dahman: DC resistance in ohms, per phase. (Values for ungrounded delta windings are generally not needed as these are open circuits to GIC.)

## Transformers Complete
GIC Transformers
Sub Name High | Nom kV High | Nom kV Med | Nom kV Ter | Bus Num High | Bus Name High | Bus Num Med | Bus Name Med | Bus Num Ter | Bus Name Ter | Circuit | GIC Blocked for Transformer Neutral | Manually Enter Coil Resistance | Coil Resistance (Ohms) for High winding | Coil Resistance (Ohms) for Medium winding | Coil Resistance (Ohms) for Tertiary winding | Transformer Neutral Resistance (Ohms) | XF Config High | XF Config Med | XF Config Ter | Is Autotransformer | Core Type | GIC Model Type | GIC Model First Segment Slope | GIC Model Param Break Point | GIC Model Param Second Segment Slope
Springfield | 345 | 18 |  | 1 | Springfield1 | 2 | Springfield2 | 0 |  | 1 | NO | Yes | 0.138 | 0.0012 | 0.005 | 0.1 | Gwye | Delta | Delta | NO | Single Phase | Default | 0 | 0 | 1.85
Note on A1: Scott R. Dahman: More complete format for pasting directly into PowerWorld Simulator GIC Transformer records. Yellow fields are most essential; green fields are optional
Note on L2: Scott R. Dahman: Is a capacitive blocking device in series with the transformer neutral?
Note on M2: Scott R. Dahman: Are the coil resistances user-supplied or estimated from the AC per-unit value
Note on N2: Scott R. Dahman: DC resistance in ohms, per phase. (Values for ungrounded delta windings are generally not needed as these are open circuits to GIC.)
Note on O2: Scott R. Dahman: DC resistance in ohms, per phase. (Values for ungrounded delta windings are generally not needed as these are open circuits to GIC.)
Note on P2: Scott R. Dahman: DC resistance in ohms, per phase. (Values for ungrounded delta windings are generally not needed as these are open circuits to GIC.)
Note on T2: Scott R. Dahman: normally assumed to be delta connected and open circuit to GIC
Note on X2: Scott R. Dahman: per-unit K-Factor
Note on Y2: Scott R. Dahman: Per-Unit reactive power (Q) breakpoint in 2-segment piecewise-linear K-Factor
Note on Z2: Scott R. Dahman: per-unit K-Factor

## Transformer Options
Configuration | Core Type | Is Autotransformer | Manually Enter Coil Resistance | GIC Model Type | GIC Blocked for Transformer Neutral
Wye | Single Phase | Yes | Yes | Default | Yes
GWye | Three Phase Shell Generic | No | No | Piecewise Linear | No
Delta | 3-legged, Three Phase | Unknown
Shunt Wye | 5-legged, Three Phase
Shunt GWye | 7-legged, Three Phase
Shunt Delta | Core, Three Phase Generic
Unknown | Unknown
Note on K1: Scott R. Dahman: Is a capacitive blocking device in series with the transformer neutral?
Note on G2: Scott R. Dahman: Coil resistance will be derived from per-unit impedance in the load flow model
Note on I2: Scott R. Dahman: K-factor will be derived from nominal voltage and core type
Note on G3: Scott R. Dahman: User-specified values will be used
Note on I3: Scott R. Dahman: K-factor will be user-specified value in "GIC Model Param"

## Switched Shunts
Shunt
Sub Name of Bus | Number of Bus | ID | Resistance Per Phase in Ohms | Scale Conductance | Neutral Resistance (Ohms)
Springfield | 1 | 1 | 0.1 | YES | 0.1
Note on A1: Scott R. Dahman: For pasting directly into PowerWorld Simulator Switched Shunt records. Yellow fields are most essential; green fields are optional. If no data is entered, shunt is assumed to have infinite resistance. Zero values are treated as infinite resistance. No data is needed for shunts that are always capacitive. Capacitive shunts are always assumed to be open circuits to GIC.
Note on D2: Scott R. Dahman: Total resistance for all three phases is one thrid this value. The resistance is ignored when the switched shunt value is capacitive.
Note on E2: Scott R. Dahman: If YES, conductance value is scaled based on the percentage of reactors that are actually connected. The resistance field then gives the minimum resistance (maximum conductance).
Note on F2: Scott R. Dahman: 3-phase value. The Neutral Resistance models any extra resistance in the switched shunt neutral; hence it is in series with the 3-phase resistance of the reactor.

## Line Shunts
LineShunt
Sub Name | Sub Name | From Number | To Number | Circuit | Bus Number Located At | ID | Status Shunt | Resistance Per Phase in Ohms
Springfield | Champaign | 1 | 3 | 1 | 3 | 1 | Closed | 0.1
Note on I2: Scott R. Dahman: Zero values are treated as infinite.

## Transmission Lines
Branch
From Sub Name | To Sub Name | From Number | From Name | To Number | To Name | Circuit | Manually Enter Line Resistance | Custom DC Resistance (Ohms/Phase)
Springfield | Champaign | 1 | Springfield1 | 3 | Champaign1 | 1 | YES | 3.5
Note on H2: Scott R. Dahman: Default is NO, in which case skin effect at 60 Hz is assumed negligible and resistance is calculated from AC per-unit R.